## Sheet1
a. | Analytical and Numerical Model Solutions
| Total Population = | 500
| Water Consumed = | 90000 | LPCD
|  | 90 | KLD
|  | 0.09 | MLD
|  | 90 | m3/day
| Average Sewage generated = | 76.5 | KLD
| Average Sewage per hour = | 3.1875 | m3/hour
| Peak Factor = | 3
| Design Flow Capacity = | 9.5625 | m3/hour
|  | 0.0027 | m3/sec
b. | Sizing Calculation for Collection Pit
| Retention time required = | 4 | hr
| Average Design flow = | 3.1875 | m3/hour
| Capacity of collection sump = | 12.75 | m3
| Assume liquid depth = | 5 | m
| Area, required for collection pit = | 2.55 | m2
Let us consider it to be a circular tank
Now,
| r = | 0.9 | m
c. | Design of Sewer Chamber
| Qmax | 0.0027 | m3/sec
Assumption,
| Shape of Bar | MS FLAT
| Size | 10 | mm
|  | 50 | mm
| Clear Spacing between the bars = | 20 | mm
| Inclination of bars | 80 | deg
|  | 1.4 | radian
| Sin 80 | 0.98545
| Assume avg. velocity to sewer | 0.8 | m/sec
| At peak flow, net inclined area required = | 0.003375 | m2
| Gross inclined area | 0.00405 | m2
| Gross vertical area required | 0.0039911 | m2
| Provide submergence depth | 0.3 | m
| Width of channel | 0.013304 | m
| Assumed Width of channel | 0.3 | m
d. | Design of Grit Chamber
| Design Flow | 0.225 | MLD
|  | 225 | m3/day
| Surface Loading | 1100 | m3/m2/day
To account for turbulence and short circuiting,
| Reduced surface loading | 770 | m3/m2/day
| Area required | 0.29221 | m2
| Assumed area required | 0.3 | m2
Provide 0.3 m dia. Chamber (Circular)
| detention time | 60 | sec
| Volume | 0.15625 | m3
| Liquid Depth | 0.53 | m
| Free Board | 0.6 | m
| Size of grit chamber | 0.3 X [0.53 + 0.6]
0.3 X 1.13 m
| Dia | 0.3 | m
e. | Check for horizontal velocity
| Cross sectional area of grit chamber | 0.159 | m2
| Velocity | 0.02 | m/sec
|  | 2 | cm/sec
| Check if velocity less than 18 cm/sec | OK
| Grit generation assumed | 0.05 | m3
per
|  | 1000 | m3
of sewage flow
| Storage volume required | 0.0051 | m3
| Grit storage area | 3.14 | m2
| Grit storage depth | 0.0016 | m
| Total liquid depth | 0.53 | m
| Provide grit chamber of size | 2 m X 0.28 m
f. | Design of Primary Sedimentation Tank
| Detention time | 2 | hour
| Volume of Sewage | 1.59 | m3
| Provide depth | 1 | m
| Surface Area | = Volume/Depth
|  | 1.59 | m2
| d2 | 2.02 | m
| d | 1.42 | m
g. | Design of Aeration Tank
| No. of Tanks | 2
| Avg. Flow to each tank | 0.1125 | MLD
| Q | 112.5 | m3/day
| Total BOD entering STP | 295 | mg/L
| The BOD of sewage coming to aeration tank, Y0 | 295 | mg/L
| BOD left in the effluent, YE | 20 | mg/L
| BOD removed in the activated plant | 275 | mg/L
| Minimum efficiency required in the activated pant | 93 | %
OK
Volume of aeration tank can be designed by assuming a suitable value for MLSS and "qC" (or F/M ratio). MLSS should be between 3000 - 3500 mg/L and F/M ratio should be between 0.18 - 0.10.
Assuming,
| MLSS, XT | 3000 | mg/L
| F/M ratio, "qC" | 0.1
F/M = (Q/V) X (Y0 / XT)
| We have, Q = | 112.5 | m3/day
| Y0 = | 295 | mg/L
| XT = | 3000 | mg/L
| F/M ratio, "qC" = | 0.1
Therefore,
| V = | (Q x Y0) / (qC x XT)
| Hence, V = | 110.625 | m3
Let us adopt an aeration tank of following dimensions
| B = | 5 | m
| D = | 2 | m
| H = V/(BxD) | 11.0625 | m
| Hence, H = | 12 | m
| Volume Provided = | 120 | m3
Since, Volume provided > Required Volume,
Hence, the adopted tank size is OK.
So, the adopted tank size is (5 + 0.6)m X 2m X 12m .
h. | Design of Secondary Clarifiers
| No. of Clarifiers = | 1 | no.
| Avg. Flow = | 76.5 | m3/day
| Reduced flow, say 50 % = | 112.5 | m3/day
| Total Inflow = | 189 | m3/day
| Provide hydraulic detention time = | 2 | hrs
| Volume of tank = | 15.75 | m3
| Assume liquid depth = | 3.5 | m
| Area = | 4.5 | m2
| Surface loading area of avg. flow = | 15 | m3/m2/day
| Surface area to be provided = | 5.1 | m2
Provide area greater of the two.
| Hence, Provided Area = | 5.1 | m2
| Dia. of circular tank (d) = | 2.5477 | m
| Provided diameter = | 3 | m
Hence, provide a clarifier of 10 m dia. Having liquid depth as 3.5 m.
i. | Return Sludge Pump House
| Total return flow = | 112.5 | m3/day
|  | 4.6875 | m3/hour
|  | 0.0781 | m3/min
| Detention time = | 15 | min
| Volume of wet well = | 1.1715 | m3
| Provide wet well = | 2.5m x 1.5m x 1.8m
| Provide dry well = | 2.5m x 2.5m
| Size of annexe control room = | 2.5m x 2.5m
Provide 2nos pumps each of 0.112 MLD capacity in the dry well for returning the sludge to aeration tank. The return sludge pipe line should be 150 mm F .
j. | Design of sludge drying beds
Sludge applied for drying beds @100 Kg/MLD
| Sludge applied = | 125 | Kg/day
| Specific gravity = | 1.015
| Solid Contents = | 1.5 | %
| Volume of sludge = | 8.21 | m3/day
| Considering monsoon, etc., total no. of cycle in 1 year = | 33
| Period of each cycle = | 11 | days
| Volume of sludge = | 90.31 | m3
| Spreading a layer of 0.3 m per cycle area of beds required = | 302
Provide 4 beds of 1.2 m X 7 m,
| Thus provided area = | 336 | m2